## Heating Load
Heating Requirements | Approximate | Total Sq Ft Campus | 621436
| Building | sq ft | -BTU/h Approx | Ton | Feet of Pipe | GPM Flow
| Applied Technology | 83244 | 1914612 | 159.551 | 51694.524 | 478.653
| Business | 50966 | 1172218 | 97.6848 | 31649.886 | 293.0545
| Calice | 36837 | 847251 | 70.6042 | 22875.777 | 211.8127
| Child Care | 4896 | 112608 | 9.384 | 3040.416 | 28.152
Total |  | 621436 | 4046689 | 337.2241 | 109260.603 | 1011.6722
8.3333 | Ton/therm
23 | Loss BTU/h | [6 empty] | System for Calice | System for Campus
12000 | BTU/Ton | [5 empty] | Ton System | 100 | 1500
324 | Feet Pipe/ Ton | [5 empty] | Sq Ft | 36837 | 584599
16-23 BTU per sq ft per hour loss |  | Therm = Ton*hour |  |  |  |  | Ton / Sqft | 0.0027147 | 0.0025659
150-200 FT of pipe per ton |  | Therm/hour = Ton |  |  |  |  | Feet Pipe/ Ton | 324 | 324
1 Ton requires 2GPM flow | [6 empty] | holes | 36 | 540
8" pipe ~950 GPM Flow | [6 empty] | depth | 450 | 450
[7 empty] | feet pipe | 32400 | 486000
[7 empty] | ft/sqft | 0.87955 | 0.83134
[7 empty] | miles of pipe | 6.1364 | 92.0455 | 16.2 | W / ft of pipe
2016 Therms | 337668.3 | [8 empty] | 7873200 | W
2017 Therms | 343972.2 | [5 empty] | Wells in hexagon shape |  |  | 7.8732 | MW
2018 Therms | 390695 | [5 empty] | Closer to bedrock closer to mountain
Average Therms | 357445.1667 | [5 empty] | Location of wells
Total Ton | 2978709.71 | [5 empty] | Vertical slice of ground conditions under campus
Average YearlyTonHours | 340.0354
Winter Month Therms
Date | Days | Therm | Therm Factor | Total Therm | Therms/day | Therms/Hour | Ton
2016-02-01 | 31 | 62270 | 1.0279 | 64007.8 | 2064.8 | 86.0333 | 716.9444
2017-02-01 | 31 | 56450 | 1.0283 | 58049.9 | 1872.6 | 78.025 | 650.2083
2018-02-01 | 31 | 67500 | 1.0265 | 69289.5 | 2235.1 | 93.1292 | 776.0764
2019-02-01 | 31 | 63150 | 1.0283 | 64937.3 | 2094.8 | 87.2833 | 727.3611
Therm Loss/ Hour
∆T = ft^2 / R-Value Solve R

## Cooling Load electricity
Read |  | On-Peak | On-Peak | Off-Peak |  | Reactive | Total Usage | Power | Load | Total Cost | Cost/kWh | Usage/Day |  | NYSEG Delivery |  | NYSEG Supply
Date | Active Days | Usage (kWh) | 14 | Usage (kWh) | Total | (RKVAH) | (kWh) | Factor | Factor | ($) | ($) | (kWh) |  | Charges ($) | Rate ($/kWh) | Charges ($) | Rate ($/kWh)
2018-01-12 | 30 | 286267 | 1227.64 | 361401 | 647668 | 354200 | 647668 | 0.877 | 0.733 | 55235.92 | 0.0853 | 21589 |  | 7561.4 | 0.01167 | 47674.52 | 0.0736
2018-02-12 | 31 | 321778 | 1267.96 | 377789 | 699567 | 320600 | 699567 | 0.909 | 0.742 | 40354.55 | 0.0577 | 22567 |  | 6953.7 | 0.00994 | 33400.85 | 0.0477
2018-03-14 | 30 | 350622 | 1406.56 | 335696 | 686318 | 337400 | 686318 | 0.897 | 0.678 | 24606.81 | 0.0359 | 22877 |  | 7388.37 | 0.01077 | 17218.44 | 0.0251
2018-04-12 | 29 | 308111 | 1288.96 | 304992 | 613103 | 292600 | 613103 | 0.902 | 0.683 | 29341.36 | 0.0479 | 21141 |  | 7952.01 | 0.01297 | 21389.35 | 0.0349
2018-05-11 | 29 | 316185 | 1571.24 | 277481 | 593666 | 309400 | 593666 | 0.887 | 0.543 | 40691.97 | 0.0685 | 20471 |  | 9495.54 | 0.01599 | 31196.43 | 0.0525
2018-06-13 | 33 | 326400 | 1447.68 | 335588 | 661988 | 361200 | 661988 | 0.878 | 0.577 | 41284.79 | 0.0624 | 20060 |  | 13132.16 | 0.01984 | 28152.63 | 0.0425
2018-07-13 | 30 | 342316 | 1508.6 | 329997 | 672313 | 438200 | 672313 | 0.838 | 0.619 | 43452.46 | 0.0646 | 22410 |  | 11271.05 | 0.01676 | 32181.41 | 0.0479
2018-08-14 | 32 | 393647 | 1639.24 | 578926 | 972573 | 463400 | 972573 | 0.903 | 0.773 | 52019.76 | 0.0535 | 30393 |  | 12792.93 | 0.01315 | 39226.83 | 0.0403
2018-09-13 | 30 | 451531 | 1992.88 | 444187 | 895718 | 526400 | 895718 | 0.862 | 0.624 | 57734.81 | 0.0645 | 29857 |  | 13363.78 | 0.01492 | 44371.03 | 0.0495
2018-10-11 | 28 | 388916 | 1800.96 | 375527 | 764443 | 428400 | 764443 | 0.872 | 0.632 | 48511.77 | 0.0635 | 27302 |  | 11482.05 | 0.01502 | 37029.72 | 0.0484
2018-11-13 | 33 | 367209 | 1408.64 | 370877 | 738086 | 366800 | 738086 | 0.896 | 0.662 | 42001.81 | 0.0569 | 22366 |  | 9094.83 | 0.01232 | 32906.98 | 0.0446
2018-12-13 | 30 | 337662 | 1019.3 | 353322 | 690984 | 482454 | 690984 | 0.82 | 0.942 |  | 0 | 23033 |  | 7520.1 | 0.01088 | 32021.06 | 0.0463
TOTAL | 365 | 4190644 | 1992.88 | 4445783 | 8636427 | 4681054 | 8636427 | 0.879 | 0.495 | 475236.01 | 0.055 | 23661 |  | 118008 | 0.01366 | 396769 | 0.0459
Building | Area | %sq area | Energy Consumption (kWh) | Convert KWh to BTU | Year of Const / Reno | Efficiency Coefficient | Efficiency (Now) | Efficiency (geo)
Applied Technology | 83244 | 13.4% | 1156886.195 | 3947295696 | 1984 | 1.25 | 0.7
BC Center (Child Care) | 4863 | 0.7825% | 67583.7005 | 230595586.1 |  |  | 0.7
Business | 50996 | 8.206% | 708718.5668 | 2418147750 | 1971 |  | 0.7
Calice Advanced Manuf | 36837 | 5.928% | 511943.4043 | 1746750895 | 2019 | 0.7 | 4.5
Campus Services | 23659 | 3.807% | 328801.7212 | 1121871473 | 1992 |  | 0.7
Decker Health | 70635 | 11.37% | 981652.2074 | 3349397332 | 1998 |  | 0.7
Ice Center | 58793 | 9.461% | 817077.6276 | 2787868866 |  |  | 0.7
Library | 49194 | 7.916% | 683675.2133 | 2332699828 | 1968 |  | 0.7
Natural Science (estim) | 36000 | 5.793% | 500311.1696 | 1707061711 | 2013 |  | 0.7
Old Science | 35925 | 5.781% | 499268.8547 | 1703505332 |  |  | 0.7
Public Safety | 10314 | 1.66% | 143339.1501 | 489073180.1 |  |  | 0.7
Student Center | 73221 | 11.78% | 1017591.226 | 3472021264 |  |  | 0.7
Student Services | 20140 | 3.241% | 279896.3043 | 955006190.4 |  |  | 0.7
Titchener Hall | 44926 | 7.229% | 624360.5446 | 2130318178 |  |  | 0.7
Wales Center | 22689 | 3.651% | 315321.1146 | 1075875643 | 2014 |  | 0.7
| 621436 |  | 8636427 | 29467488924
Electric consumption (MWh) 2017 | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Space Cooling | 0.08 | 0 | 0.1 | 0.88 | 3.26 | 5.6 | 9.05 | 13.14 | 5.05 | 1.19 | 0.02 | 0 | 38.37
Heat Rejection
Refrigeration
Space Heating | 18.89 | 21.81 | 8.63 | 6.6 | 0.8 | 0.02 | 0.01 | 0.01 | 0.02 | 2.6 | 11.18 | 8.46 | 79.03
Heat Pump Supp. | 29467488924 Total: 0
Hot Water | 29467488924 Total: 0
Vent Fans | 1.55 | 1.84 | 1.55 | 1.85 | 1.94 | 0.97 | 1.18 | 2.13 | 1.26 | 1.56 | 1.94 | 0.87 | 18.64
Pumps and Aux. | 2.77 | 3.29 | 2.77 | 2.04 | 3.4 | 1.79 | 2.08 | 3.6 | 2.23 | 2.6 | 3.4 | 1.56 | 31.53
Geothermal Pumnps | 29467488924 Total: 0
Exterior Usage | 29467488924 Total: 0
Misc Equipment (Ice Maker) | 7.61 | 7.94 | 7.91 | 7.32 | 8.42 | 4.64 | 5.58 | 9.43 | 5.96 | 7.01 | 6.38 | 4.53 | 82.73
Task Lighting | 29467488924 Total: 0
Area Lighting | 17.65 | 20.01 | 17.65 | 15.44 | 21.23 | 12.15 | 14.05 | 23.01 | 14.87 | 17.65 | 21.12 | 11.4 | 206.23
Total | 48.55 | 54.89 | 38.61 | 34.13 | 39.05 | 25.17 | 31.95 | 51.32 | 29.39 | 32.61 | 44.04 | 26.82 | 456.53

## Square Footage
Square Ft of Bore Area | sq ft | m2 | m2/100 | Spacing Feet | Spacing (m) | BPZ Hexagon Layout
Zone A (Back Creek) | 480139 | 44606.3727 | 446.0637 | 20 | 6.0957 | 1397 | Calice System
Zone B (Back Parking) | 115390 | 10720.0818 | 107.2008 | 20 | 6.0957 | 323 | 6420
Zone C (Alumni Field) | 142662 | 13253.7335 | 132.5373 | 20 | 6.0957 | 409 | 36
Zone D (Science Parking Lot) | 229132 | 21287.0594 | 212.8706 | 20 | 6.0957 | 656 | 15
Baseball Field | 272732 | 25337.6319 | 253.3763 | 20 | 6.0957 | 789
Quad Remaining | 10669 | 991.1825 | 9.9118 | 20 | 6.0957 | 19
Sum | 1250724 | 116196.0618 | 1161.9606 | 20 | 6.0957 | 3593 | 0.0056075
https://www.engineeringtoolbox.com/circles-within-rectangle-d_1905.html
Total Potential Bores | 3593
Whole Campus Area | 4012000 | Sq ft
Proposed Geothermal Sites | 0.31175 | Percent Campus

## FlowRate Temp
Summer Temp
MW | KW | Q (KJ/S) | m (GPM) | m (KG/S) | c (KJ/KG C) |  | T1 (F) Supply | T1(C) | T2 (C) | T2 (F) Return | Delta T (F)
13.14 |  | 13140 | 400 | 25.2366 | 4.186 | Ground Temp Summer | 90 | 32.2222 | 40.0698 | 104.1257 | 14.1257
13.14 |  | 13140 | 600 | 37.8549 | 4.186 |  | 90 | 32.2222 | 37.4539 | 99.4171 | 9.4171
13.14 |  | 13140 | 800 | 50.4732 | 4.186 |  | 90 | 32.2222 | 36.146 | 97.0628 | 7.0628
13.14 |  | 13140 | 1000 | 63.0915 | 4.186 |  | 90 | 32.2222 | 35.3613 | 95.6503 | 5.6503
13.14 |  | 13140 | 1200 | 75.7098 | 4.186 |  | 90 | 32.2222 | 34.8381 | 94.7086 | 4.7086 | 8" pipe for summer
13.14 |  | 13140 | 1400 | 88.3281 | 4.186 |  | 90 | 32.2222 | 34.4644 | 94.0359 | 4.0359
13.14 |  | 13140 | 1600 | 100.9464 | 4.186 |  | 90 | 32.2222 | 34.1841 | 93.5314 | 3.5314
13.14 |  | 13140 | 1800 | 113.5647 | 4.186 |  | 90 | 32.2222 | 33.9661 | 93.139 | 3.139
13.14 |  | 13140 | 2000 | 126.183 | 4.186 |  | 90 | 32.2222 | 33.7917 | 92.8251 | 2.8251
Winter Temp
MWh | KW
21.81 |  | -21810 | 400 | 25.2366 | 4.186 | Ground Temp Winter | 40 | 4.4444 | -8.5811 | 16.554 | -23.446
21.81 |  | -21810 | 600 | 37.8549 | 4.186 |  | 40 | 4.4444 | -4.2393 | 24.3693 | -15.6307
21.81 |  | -21810 | 800 | 50.4732 | 4.186 |  | 40 | 4.4444 | -2.0683 | 28.277 | -11.723
21.81 |  | -21810 | 1000 | 63.0915 | 4.186 |  | 40 | 4.4444 | -0.76578 | 30.6216 | -9.3784
21.81 |  | -21810 | 1200 | 75.7098 | 4.186 |  | 40 | 4.4444 | 0.10259 | 32.1847 | -7.8153
21.81 |  | -21810 | 1400 | 88.3281 | 4.186 |  | 40 | 4.4444 | 0.72286 | 33.3011 | -6.6989
21.81 |  | -21810 | 1600 | 100.9464 | 4.186 |  | 40 | 4.4444 | 1.1881 | 34.1385 | -5.8615 | 10" pipe for winter
21.81 |  | -21810 | 1800 | 113.5647 | 4.186 |  | 40 | 4.4444 | 1.5499 | 34.7898 | -5.2102
21.81 |  | -21810 | 2000 | 126.183 | 4.186 |  | 40 | 4.4444 | 1.8393 | 35.3108 | -4.6892
10" pipe
https://inventory.powerzone.com/item/56946/used-sulzer-bingham-8x10x125-cp-d-horizontal-multi-stage-centrifugal-pump-complete-pump
10" Pipe
21.81 |  | -21810 | 1400 | 88.3281 | 4.186 |  | 68 | 20 | 16.2784 | 61.3011 | -6.6989
13.14 |  | 13140 | 1400 | 88.3281 | 4.186 |  | 86 | 30 | 32.2422 | 90.0359 | 4.0359
cooling Data
January |  | 0 | 1400 | 88.3281 | 4.186 |  | 40 | 4.4444 | 4.4444 | 40 | 0
February |  | 0 | 1400 | 88.3281 | 4.186 |  | 40 | 4.4444 | 4.4444 | 40 | 0
March |  | 0 | 1400 | 88.3281 | 4.186 |  | 86 | 30 | 30 | 86 | 0
April | 0.88 | 880 | 1400 | 88.3281 | 4.186 |  | 86 | 30 | 30.1502 | 86.2703 | 0.27029
May | 3.26 | 3260 | 1400 | 88.3281 | 4.186 |  | 86 | 30 | 30.5563 | 87.0013 | 1.0013
June | 5.6 | 5600 | 1400 | 88.3281 | 4.186 |  | 86 | 30 | 30.9556 | 87.72 | 1.72
July | 9.05 | 9050 | 1400 | 88.3281 | 4.186 |  | 86 | 30 | 31.5443 | 88.7797 | 2.7797
August | 13.14 | 13140 | 1400 | 88.3281 | 4.186 |  | 86 | 30 | 32.2422 | 90.0359 | 4.0359
September | 5.05 | 5050 | 1400 | 88.3281 | 4.186 |  | 86 | 30 | 30.8617 | 87.5511 | 1.5511
October | 1.19 | 1190 | 1400 | 88.3281 | 4.186 |  | 86 | 30 | 30.2031 | 86.3655 | 0.3655
November |  | 0 | 1400 | 88.3281 | 4.186 |  | 86 | 30 | 30 | 86 | 0
December |  | 0 | 1400 | 88.3281 | 4.186 |  | 86 | 30 | 30 | 86 | 0

## Loop Temperature Across Year
Loop Temp Modelled With 50F
| Ground Exchange | Ice Rink | Space Heating (Electric MWh) | Area Lighting | Space Cooling | All Gas Usage
|  |  |  | MWh | MWh | MWh | Sum MWh | Q (KJ/S) | m (GPM) | m (KG/S) | c (KJ/KG C) | T1 (F) Supply | T1(C) | T2 (C) | T2 (F) Return | Delta T (F)
January | 70 | 7.61 | 18.89 | 17.65 |  | 0 | 114.15 | 114150 | 100 | 6.3091 | 4.186 | 36.6163 | 2.5646 | 2.8373 | 37.1071 | 0.49085
February | 70 | 7.94 | 21.81 | 20.01 |  | 0 | 119.76 | 119760 | 100 | 6.3091 | 4.186 | 37.0052 | 2.7807 | 3.0668 | 37.5202 | 0.51497
March | 70 | 7.91 | 8.63 | 17.65 |  | 0 | 104.19 | 104190 | 100 | 6.3091 | 4.186 | 41.9892 | 5.5496 | 5.7985 | 42.4373 | 0.44802
April | 70 | 7.32 | 6.6 | 15.44 | 0.88 | 0 | 100.24 | 100240 | 100 | 6.3091 | 4.186 | 48.0451 | 8.914 | 9.1534 | 48.4762 | 0.43104
May | 70 | 8.42 | 0.8 | 21.23 | 3.26 | 0 | 103.71 | 103710 | 100 | 6.3091 | 4.186 | 53.7936 | 12.1076 | 12.3553 | 54.2396 | 0.44596
June | 70 | 4.64 | 0.02 | 12.15 | 5.6 | 0 | 92.41 | 92410 | 100 | 6.3091 | 4.186 | 58.309 | 14.6161 | 14.8369 | 58.7064 | 0.39737
July | 70 | 5.58 | 0.01 | 14.05 | 9.05 | 0 | 98.69 | 98690 | 100 | 6.3091 | 4.186 | 59.0827 | 15.0459 | 15.2817 | 59.507 | 0.42437
August | 70 | 9.43 | 0.01 | 23.01 | 13.14 | 0 | 115.59 | 115590 | 100 | 6.3091 | 4.186 | 58.4711 | 14.7062 | 14.9823 | 58.9681 | 0.49704
September | 70 | 5.96 | 0.02 | 14.87 | 5.05 | 0 | 95.9 | 95900 | 100 | 6.3091 | 4.186 | 53.7049 | 12.0583 | 12.2874 | 54.1172 | 0.41237
October | 70 | 7.01 | 2.6 | 17.65 | 1.19 | 0 | 98.45 | 98450 | 100 | 6.3091 | 4.186 | 49.627 | 9.7928 | 10.028 | 50.0504 | 0.42334
November | 70 | 6.38 | 11.18 | 21.12 |  | 0 | 108.68 | 108680 | 100 | 6.3091 | 4.186 | 44.934 | 7.1856 | 7.4452 | 45.4014 | 0.46733
December | 70 | 4.53 | 8.46 | 11.4 |  | 0 | 94.39 | 94390 | 100 | 6.3091 | 4.186 | 39.0659 | 3.9255 | 4.151 | 39.4717 | 0.40588
Loop Temp Modelled with 60F
| Ground Exchange (MWh) | Ice Rink | Space Heating (Electric MWh) | Area Lighting | Space Cooling | All Gas Usage
Month |  |  |  | MWh | MWh | MWh | Sum MWh | Q (KJ/S) | m (GPM) | m (KG/S) | c (KJ/KG C) | T1 (F) Supply | T1(C) | T2 (C) | T2 (F) Return | Delta T (F)
January | 7.8732 | 7.61 | 18.89 | 17.65 |  | -334.439 | -282.4158 | -282415.82 | 100 | 6.3091 | 4.186 | 41.6163 | 5.3424 | 4.6677 | 40.4019 | -1.2144 | -2.4496
February | 7.8732 | 7.94 | 21.81 | 20.01 |  | -336.6894 | -279.0562 | -279056.22 | 100 | 6.3091 | 4.186 | 42.0052 | 5.5584 | 4.8918 | 40.8053 | -1.2 | 0.38894
March | 7.8732 | 7.91 | 8.63 | 17.65 |  | -265.1667 | -223.1035 | -223103.52 | 100 | 6.3091 | 4.186 | 46.9892 | 8.3274 | 7.7944 | 46.0299 | -0.95936 | 4.984
April | 7.8732 | 7.32 | 6.6 | 15.44 | 0.88 | -322.2747 | -284.1615 | -284161.48 | 100 | 6.3091 | 4.186 | 53.0451 | 11.6917 | 11.0129 | 51.8232 | -1.2219 | 6.0559
May | 7.8732 | 8.42 | 0.8 | 21.23 | 3.26 | -130.7465 | -89.1633 | -89163.3 | 100 | 6.3091 | 4.186 | 58.7936 | 14.8853 | 14.6723 | 58.4102 | -0.38341 | 5.7485
June | 7.8732 | 4.64 | 0.02 | 12.15 | 5.6 | -85.9983 | -55.7151 | -55715.14 | 100 | 6.3091 | 4.186 | 63.309 | 17.3939 | 17.2608 | 63.0695 | -0.23958 | 4.5154
July | 7.8732 | 5.58 | 0.01 | 14.05 | 9.05 | -33.2259 | 3.3373 | 3337.32 | 100 | 6.3091 | 4.186 | 64.0827 | 17.8237 | 17.7443 | 63.9398 | -0.14287 | 0.77363
August | 7.8732 | 9.43 | 0.01 | 23.01 | 13.14 | -21.8556 | 31.6076 | 31607.64 | 100 | 6.3091 | 4.186 | 63.4711 | 17.4839 | 17.5595 | 63.607 | 0.13591 | -0.61156
September | 7.8732 | 5.96 | 0.02 | 14.87 | 5.05 | -49.2292 | -15.456 | -15456.04 | 100 | 6.3091 | 4.186 | 58.7049 | 14.836 | 14.7991 | 58.6384 | -0.066462 | -4.7662
October | 7.8732 | 7.01 | 2.6 | 17.65 | 1.19 | -77.7942 | -41.471 | -41471.04 | 100 | 6.3091 | 4.186 | 54.627 | 12.5706 | 12.4715 | 54.4487 | -0.17833 | -4.0778
November | 7.8732 | 6.38 | 11.18 | 21.12 |  | -107.0204 | -60.4672 | -60467.24 | 100 | 6.3091 | 4.186 | 49.934 | 9.9633 | 9.8189 | 49.674 | -0.26001 | -4.693
December | 7.8732 | 4.53 | 8.46 | 11.4 |  | -230.5987 | -198.3355 | -198335.52 | 100 | 6.3091 | 4.186 | 44.0659 | 6.7033 | 6.2294 | 43.213 | -0.85285 | -5.8682
http://www.heat-balance.com/

## Heating Days Data
Month Number
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
|  |  | January | February | March | April | May | June | July | August | September | October | November | December | Total | Energy Consumption | Demand | Dew Point | Rel H (%) | Wet Bulb (°F) | Enthalpy (BTU/lbm)
|  | Average Loop Temp (F) | 45 | 48 | 50 | 54 | 58 | 66 | 72 | 76 | 70 | 62 | 54 | 53
|  | Cooling (MWh) | Month Number 4: 0.88; Month Number 5: 3.26; Month Number 6: 5.6; Month Number 7: 9.05; Month Number 8: 13.14; Month Number 9: 5.05; Month Number 10: 1.19
90 | 95 |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 69.98 | 48.667 | 75.905 | 40.504
85 | 90 |  | 0 | 0 | 0 | 0 | 1 | 24 | 13 | 7 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 67.64 | 52.578 | 73.3 | 37.94
80 | 85 |  | 0 | 0 | 0 | 0 | 11 | 46 | 74 | 41 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 63.204 | 54.017 | 69.275 | 34.404
75 | 80 |  | 0 | 0 | 0 | 0 | 35 | 73 | 106 | 91 | 17 | 0 | 0 | 0 | 322 | 0 | 0 | 60.177 | 58.137 | 65.976 | 31.676
70 | 75 |  | 0 | 0 | 0 | 0 | 38 | 95 | 93 | 111 | 41 | 0 | 0 | 0 | 378 | 0 | 0 | 57.42 | 61.619 | 63.033 | 29.408
65 | 70 |  | 0 | 0 | 0 | 3 | 77 | 150 | 172 | 123 | 72 | 9 | 0 | 0 | 606 | 4.5849 | 0 | 56.437 | 68.807 | 60.927 | 27.863
|  | Heating (MMBTU) | 5764.81 | 5803.6 | 4570.75 | 5555.13 | 2253.71 | 1482.38 | 572.72 | 376.73 | 848.58 | 1340.96 | 1844.74 | 3974.89 | 34389
60 | 65 |  |  | 0 | 9 | 48 | 121 | 198 | 153 | 231 | 168 | 104 | 5 | 0 | 1037 |  |  | 52.824 | 73.583 | 57.008 | 25.178
55 | 60 |  | 0 | 0 | 38 | 60 | 161 | 63 | 81 | 110 | 160 | 113 | 48 | 2 | 836 |  |  | 48.683 | 76.344 | 52.586 | 22.353
50 | 55 |  | 0 | 0 | 42 | 98 | 130 | 27 | 34 | 26 | 87 | 96 | 39 | 5 | 584 |  |  | 42.342 | 71.471 | 47.486 | 19.418
45 | 50 |  | 43 | 1 | 47 | 192 | 79 | 25 | 17 | 2 | 120 | 169 | 68 | 21 | 784 |  |  | 38.46 | 72.364 | 43.484 | 17.297
40 | 45 | 3.74 | 37 | 26 | 42 | 152 | 70 | 17 | 0 | 0 | 31 | 143 | 113 | 27 | 658 |  |  | 33.043 | 69.906 | 38.637 | 14.921
35 | 40 | 3.36 | 52 | 35 | 119 | 113 | 19 | 2 | 0 | 0 | 24 | 71 | 238 | 118 | 791 |  |  | 28.334 | 71.197 | 33.738 | 12.731
30 | 35 | 3.35 | 114 | 129 | 194 | 30 | 2 | 0 | 0 | 0 | 0 | 32 | 176 | 166 | 843 |  |  | 23.771 | 73.484 | 28.856 | 10.657
25 | 30 |  | 76 | 130 | 94 | 11 | 0 | 0 | 0 | 0 | 0 | 7 | 33 | 108 | 459 |  |  | 19.319 | 72.094 | 24.899 | 9.069
20 | 25 |  | 138 | 112 | 65 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 459 |  |  | 13.643 | 67.627 | 20.435 | 7.397
15 | 20 |  | 79 | 134 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 410 |  |  | 8.668 | 68.544 | 15.406 | 5.641
10 | 15 |  | 79 | 57 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 185 |  |  | 4.204 | 71.503 | 10.422 | 4.016
5 | 10 |  | 58 | 41 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 113 |  |  | -0.069 | 70.628 | 6.381 | 2.765
0 | 5 |  | 43 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 |  |  | -3.489 | 74.42 | 1.953 | 1.457
-5 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 |  |  | -6.833 | 76.579 | -1.91 | 0.348
-10 | -5 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 |  |  | -10.48 | 81.5 | -6.815 | -1.023
|  |  | Month Number 12: Total | 43150

## Sheet2
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Cooling | COP | January | February | March | April | May | June | July | August | September | October | November | December | Total
65-70 |  | 0 | 0 | 0 | 0.88 | 1.54 | 2.16 | 3.39 | 4.31 | 2.8 | 1.19 | 0 | 0 | 16.27
70-75 |  | 0 | 0 | 0 | 0 | 0.76 | 1.37 | 1.83 | 3.89 | 1.59 | 0 | 0 | 0 | 9.44
75-80 |  | 0 | 0 | 0 | 0 | 0.7 | 1.05 | 2.09 | 3.19 | 0.66 | 0 | 0 | 0 | 7.69
80-85 |  | 0 | 0 | 0 | 0 | 0.22 | 0.66 | 1.46 | 1.44 | 0 | 0 | 0 | 0 | 3.78
85-90 |  | 0 | 0 | 0 | 0 | 0.02 | 0.35 | 0.26 | 0.25 | 0 | 0 | 0 | 0 | 0.88
90-95 |  | 0 | 0 | 0 | 0 | 0.02 | 0 | 0.02 | 0.07 | 0 | 0 | 0 | 0 | 0.11
Heating (MMBTU) | COP | January | February | March | April | May | June | July | August | September | October | November | December | Total
60-65 |  | 0 | 0 | 55.29 | 371.89 | 468.55 | 884.07 | 307.46 | 235.84 | 241.63 | 189.74 | 12.81 | 0 | 1037
55-60 |  | 0 | 0 | 233.45 | 464.86 | 623.45 | 281.3 | 162.77 | 112.3 | 230.12 | 206.16 | 122.98 | 10.69 | 836
50-55 |  | 0 | 0 | 258.03 | 759.28 | 503.41 | 120.56 | 68.32 | 26.54 | 125.13 | 175.15 | 99.92 | 26.71 | 584
5-10 |  | 333.18 | 8.64 | 288.74 | 1487.57 | 305.92 | 111.63 | 34.16 | 2.04 | 172.59 | 308.33 | 174.23 | 112.19 | 113
45-50 |  | 286.69 | 224.54 | 258.03 | 1177.66 | 271.06 | 75.91 | 0 | 0 | 44.59 | 260.89 | 289.52 | 144.25 | 784
40-45 |  | 402.92 | 302.27 | 731.07 | 875.49 | 73.57 | 8.93 | 0 | 0 | 34.52 | 129.53 | 609.79 | 630.43 | 658
35-40 |  | 883.32 | 1114.08 | 1191.84 | 232.43 | 7.74 | 0 | 0 | 0 | 0 | 58.38 | 450.94 | 886.87 | 791
30-35 |  | 588.88 | 1122.72 | 577.49 | 85.23 | 0 | 0 | 0 | 0 | 0 | 12.77 | 84.55 | 577 | 843
25-30 |  | 1069.28 | 967.27 | 399.33 | 100.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 699.88 | 459
20-25 |  | 612.12 | 1157.27 | 430.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 678.51 | 459
15-20 |  | 612.12 | 492.27 | 110.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.62 | 410
10-15 |  | 449.41 | 354.09 | 36.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.74 | 185
0-5 |  | 333.18 | 60.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50
-5-10 |  | 147.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
-5-0 |  | 46.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19

## Sheet9
Column1 | January | February | March | April | May | June | July | August | September | October | November | December
90-95 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0.02 | 0.07 | 0 | 0 | 0 | 0
85-90 | 0 | 0 | 0 | 0 | 0.02 | 0.35 | 0.26 | 0.25 | 0 | 0 | 0 | 0
80-85 | 0 | 0 | 0 | 0 | 0.22 | 0.66 | 1.46 | 1.44 | 0 | 0 | 0 | 0
75-80 | 0 | 0 | 0 | 0 | 0.7 | 1.05 | 2.09 | 3.19 | 0.66 | 0 | 0 | 0
70-75 | 0 | 0 | 0 | 0 | 0.76 | 1.37 | 1.83 | 3.89 | 1.59 | 0 | 0 | 0
65-70 | 0 | 0 | 0 | 0.88 | 1.54 | 2.16 | 3.39 | 4.31 | 2.8 | 1.19 | 0 | 0
60-65 | 0 | 0 | -55.29 | -371.89 | -468.55 | -884.07 | -307.46 | -235.84 | -241.63 | -189.74 | -12.81 | 0
55-60 | 0 | 0 | -233.45 | -464.86 | -623.45 | -281.3 | -162.77 | -112.3 | -230.12 | -206.16 | -122.98 | -10.69
50-55 | 0 | 0 | -258.03 | -759.28 | -503.41 | -120.56 | -68.32 | -26.54 | -125.13 | -175.15 | -99.92 | -26.71
5-10 | -333.18 | -8.64 | -288.74 | -1487.57 | -305.92 | -111.63 | -34.16 | -2.04 | -172.59 | -308.33 | -174.23 | -112.19
45-50 | -286.69 | -224.54 | -258.03 | -1177.66 | -271.06 | -75.91 | 0 | 0 | -44.59 | -260.89 | -289.52 | -144.25
40-45 | -402.92 | -302.27 | -731.07 | -875.49 | -73.57 | -8.93 | 0 | 0 | -34.52 | -129.53 | -609.79 | -630.43
35-40 | -883.32 | -1114.08 | -1191.84 | -232.43 | -7.74 | 0 | 0 | 0 | 0 | -58.38 | -450.94 | -886.87
30-35 | -588.88 | -1122.72 | -577.49 | -85.23 | 0 | 0 | 0 | 0 | 0 | -12.77 | -84.55 | -577
25-30 | -1069.28 | -967.27 | -399.33 | -100.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -699.88
20-25 | -612.12 | -1157.27 | -430.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -678.51
15-20 | -612.12 | -492.27 | -110.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -165.62
10-15 | -449.41 | -354.09 | -36.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -42.74
0-5 | -333.18 | -60.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-5-10 | -147.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-5-0 | -46.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | -5764.81 | -5803.6 | -4570.75 | -5554.25 | -2250.44 | -1476.81 | -563.66 | -363.57 | -843.53 | -1339.76 | -1844.74 | -3974.89
January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -333.18 | -286.69 | -402.92 | -883.32 | -588.88 | -1069.28 | -612.12 | -612.12 | -449.41 | -333.18 | -147.22 | -46.49
February | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.64 | -224.54 | -302.27 | -1114.08 | -1122.72 | -967.27 | -1157.27 | -492.27 | -354.09 | -60.45 | 0 | 0
March | 0 | 0 | 0 | 0 | 0 | 0 | -55.29 | -233.45 | -258.03 | -288.74 | -258.03 | -731.07 | -1191.84 | -577.49 | -399.33 | -430.04 | -110.58 | -36.86 | 0 | 0 | 0
April | 0 | 0 | 0 | 0 | 0 | 0.88 | -371.89 | -464.86 | -759.28 | -1487.57 | -1177.66 | -875.49 | -232.43 | -85.23 | -100.72 | 0 | 0 | 0 | 0 | 0 | 0
May | 0.02 | 0.02 | 0.22 | 0.7 | 0.76 | 1.54 | -468.55 | -623.45 | -503.41 | -305.92 | -271.06 | -73.57 | -7.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 0 | 0.35 | 0.66 | 1.05 | 1.37 | 2.16 | -884.07 | -281.3 | -120.56 | -111.63 | -75.91 | -8.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 0.02 | 0.26 | 1.46 | 2.09 | 1.83 | 3.39 | -307.46 | -162.77 | -68.32 | -34.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 0.07 | 0.25 | 1.44 | 3.19 | 3.89 | 4.31 | -235.84 | -112.3 | -26.54 | -2.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 0 | 0 | 0 | 0.66 | 1.59 | 2.8 | -241.63 | -230.12 | -125.13 | -172.59 | -44.59 | -34.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 0 | 0 | 0 | 0 | 0 | 1.19 | -189.74 | -206.16 | -175.15 | -308.33 | -260.89 | -129.53 | -58.38 | -12.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 0 | 0 | 0 | 0 | 0 | 0 | -12.81 | -122.98 | -99.92 | -174.23 | -289.52 | -609.79 | -450.94 | -84.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.69 | -26.71 | -112.19 | -144.25 | -630.43 | -886.87 | -577 | -699.88 | -678.51 | -165.62 | -42.74 | 0 | 0 | 0

## Sheet10
Month Number
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
[5 empty] | January | February | March | April | May | June | July | August | September | October | November | December | Total
|  | Average | EER | COP
90 | 95 | 92.5 | 15.8 | 4.6334 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 4 | 59.0827
85 | 90 | 87.5 | 15.8 | 4.6334 | 0 | 0 | 0 | 0 | 1 | 24 | 13 | 7 | 0 | 0 | 0 | 0 | 45 | 58.7769
80 | 85 | 82.5 | 15.8 | 4.6334 | 0 | 0 | 0 | 0 | 11 | 46 | 74 | 41 | 0 | 0 | 0 | 0 | 172 | 58.4711
75 | 80 | 77.5 | 15.8 | 4.6334 | 0 | 0 | 0 | 0 | 35 | 73 | 106 | 91 | 17 | 0 | 0 | 0 | 322 | 58.3901
70 | 75 | 72.5 | 15.8 | 4.6334 | 0 | 0 | 0 | 0 | 38 | 95 | 93 | 111 | 41 | 0 | 0 | 0 | 378 | 58.309
65 | 70 | 67.5 | 15.8 | 4.6334 | 0 | 0 | 0 | 3 | 77 | 150 | 172 | 123 | 72 | 9 | 0 | 0 | 606 | 56.0513
60 | 65 | 62.5 |  | 4 | 0 | 0 | 9 | 48 | 121 | 198 | 153 | 231 | 168 | 104 | 5 | 0 | 1037 | 53.7936
55 | 60 | 57.5 |  | 4 | 0 | 0 | 38 | 60 | 161 | 63 | 81 | 110 | 160 | 113 | 48 | 2 | 836 | 53.7492
50 | 55 | 52.5 |  | 3.98 | 0 | 0 | 42 | 98 | 130 | 27 | 34 | 26 | 87 | 96 | 39 | 5 | 584 | 53.7049
45 | 50 | 47.5 |  | 3.98 | 43 | 1 | 47 | 192 | 79 | 25 | 17 | 2 | 120 | 169 | 68 | 21 | 784 | 51.6659
40 | 45 | 42.5 |  | 3.95 | 37 | 26 | 42 | 152 | 70 | 17 | 0 | 0 | 31 | 143 | 113 | 27 | 658 | 49.627
35 | 40 | 37.5 |  | 3.74 | 52 | 35 | 119 | 113 | 19 | 2 | 0 | 0 | 24 | 71 | 238 | 118 | 791 | 48.8361
30 | 35 | 32.5 |  | 3.72 | 114 | 129 | 194 | 30 | 2 | 0 | 0 | 0 | 0 | 32 | 176 | 166 | 843 | 48.0451
25 | 30 | 27.5 |  | 3.74 | 76 | 130 | 94 | 11 | 0 | 0 | 0 | 0 | 0 | 7 | 33 | 108 | 459 | 46.4896
20 | 25 | 22.5 |  | 3.74 | 138 | 112 | 65 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 459 | 44.934
15 | 20 | 17.5 |  | 3.74 | 79 | 134 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 410 | 43.4616
10 | 15 | 12.5 |  | 3.74 | 79 | 57 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 185 | 41.9892
5 | 10 | 7.5 |  | 3.36 | 58 | 41 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 113 | 40.5276
0 | 5 | 2.5 |  | 3.36 | 43 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 39.0659
-5 | 0 | -2.5 |  | 3.36 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 37.0052
-10 | -5 | -7.5 |  | 3.36 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 36.6163
|  |  |  | Weighted Mean | 23.2325 | 24.0104 | 33.9785 | 46.0903 | 57.5872 | 66.6181 | 68.1653 | 66.9422 | 57.4097 | 49.254 | 39.8681 | 28.1317
|  |  |  | Weighted St. Dev. | 12.9017 | 9.0199 | 11.62 | 8.6175 | 10.2403 | 9.7831 | 9.0939 | 8.0663 | 8.9946 | 8.9176 | 7.8572 | 9.076
|  |  |  | Average loop Temp | 41.6163 | 42.0052 | 46.9892 | 53.0451 | 58.7936 | 63.309 | 64.0827 | 63.4711 | 58.7049 | 54.627 | 49.934 | 44.0659
We have taken the weighted mean of the hours each month at a given temp range and averaged that with the year-round ground temp of 50 deg to calculate the weighted avg. loop temperature per month. This is the EWT
COP
|  |  | #ERROR! | 4.6334
4.6334
4.6334
4.6334
4.6334
4.6334
4
4
3.98
3.98
3.95
3.74
3.72
3.74
3.74
3.74
3.74
3.36
3.36
3.36
3.36

## Final Calculations
Conversions |  | Units |  |  |  | Heating Demand | Therms | BTU | MWh | BTU | Total Heating Demand |  | Cooling Demand | MWh | BTU
Btu to MMbtu | 1000000 |  |  |  |  | 2016 | 337668.3 | 33758759728 |  |  |  |  | 2017 | 38.37 | 130918440
MMBTU to MWh | 3.412 |  |  |  |  | 2017 | 343972.2 | 34388999064
Btu to MWh | 3412000 |  |  |  |  | 2018 | 390695 | 39060162390 | 79.03 | 269650360 | 39329812750
[6 empty] | CO2 120Lb/ MMBTU |  | 4687219.487
[6 empty] | Tons Co2 |  | 2343.6097
Electricity growth rate | 0.13%
lbs of CO2/MMbtu | 120 | Lbs
Target Temp 71F (Indoors) | 21 | C
COP | Cooling (COP) | Heating (COP) |  |  |  | Mean COP Values | [6 empty] | Delta 10 degree COP values
Existing System |  | 0.8 |  |  |  | COP heating ratio | 4 | Cooling COP Ratio | 1.4423 | AirSource Heat Pump COP(35C) | 2.8 |  | Heating COP of Geo | 4.5
Geothermal | 2.2 | 3.8 | [10 empty] | Cooling COP Of Geo | 4.3988
Airsource | 3 | 3 |  |  |  | Heating COP of existing Gas | 0.8 | Cooling COP Of Geo | 4.3988 | Nominal Room Temp | 22C |  | AirSource Heat Pump COP(35C) | 5
[6 empty] | Heating COP of Geo | 3.2 | Cooling cop of existing AC | 3.0499 |  |  |  | Nominal Room Temp | 22
Heating Demand Per Month (2017) |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Average Temp (F) |  | 21 | 25 | 34 | 42 | 55 | 65 | 69 | 70 | 60 | 49 | 37.75 | 28
Average Temp (C) |  | -6.1111 | -3.8889 | 1.1111 | 5.5556 | 12.7778 | 18.3333 | 20.5556 | 21.1111 | 15.5556 | 9.4444 | 3.1944 | -2.2222
Delta T(C) |  | 27.1111 | 24.8889 | 19.8889 | 15.4444 | 8.2222 | 2.6667 | 0.44444 | 0.11111 | 5.4444 | 11.5556 | 17.8056 | 23.2222
COP (heating) (update values later) |  | 4.2 | 4.4 | 4.6 | 5.4 | 6 | 7 | 7.1 | 7.2 | 6.4 | 6 | 5.5 | 4.7
COP (Cooling) (update values later) |  | 7 | 7 | 6 | 5.8 | 5 | 3.8 | 3.5 | 3.3 | 3.85 | 4.4 | 5 | 6.5
Air source COP Heating |  | 3.2 | 3.6 | 4.4 | 5.1 | 5.5 | 6.2 | 6.4 | 6.4 | 6 | 5.6 | 4.5 | 4.2
Air Source COP Cooling
Therms |  | 57661.9 | 58049.9 | 45718.4 | 55564.6 | 22542.5 | 14827.3 | 5728.6 | 3768.2 | 8487.8 | 13412.8 | 18451.8 | 39758.4 | 343972.2
MMBTU NatGas |  | 5764.8119 | 5803.6026 | 4570.7473 | 5555.132 | 2253.7112 | 1482.3756 | 572.7231 | 376.7299 | 848.5771 | 1340.9594 | 1844.739 | 3974.8898 | 34388.9991
MMBTU Geothermal |  | 1441.203 | 1813.6258 | 1428.3585 | 1735.9788 | 704.2848 | 463.2424 | 178.976 | 117.7281 | 265.1804 | 419.0498 | 576.4809 | 1242.1531 | 10386.2615
Tons CO2 eq |  | 345.8887 | 348.2162 | 0.00027424 | 0.00033331 | 0.00013522 | 8.8943e-05 | 3.4363e-05 | 2.2604e-05 | 5.0915e-05 | 8.0458e-05 | 0.00011068 | 0.00023849 | 694.1062
Electricity Increase (MWh) |  | 422.3924 | 531.5433 | 418.6279 | 508.7863 | 206.4141 | 135.7686 | 52.4549 | 34.5041 | 77.7199 | 122.8165 | 168.9569 | 364.0542 | 3044.0391
Therms to MWh (MWh) |  | 1672.1951 | 1683.4471 | 1325.8336 | 1611.3734 | 653.7325 | 429.9917 | 166.1294 | 109.2778 | 246.1462 | 388.9712 | 535.1022 | 1152.9936 | 9975.1938
Current MMBTU Per Building
Applied Technology | 13.4% | 772.2211 | 777.4173 | 612.2711 | 744.1336 | 301.8942 | 198.5705 | 76.7187 | 50.4646 | 113.6705 | 179.6272 | 247.1106 | 532.4534 | 4606.5529
BC Center (Child Care) | 0.7825% | 45.1121 | 45.4156 | 35.768 | 43.4713 | 17.6362 | 11.6002 | 4.4818 | 2.9481 | 6.6405 | 10.4936 | 14.4359 | 31.1052 | 269.1085
Business | 8.206% | 473.0694 | 476.2526 | 375.0826 | 455.8627 | 184.943 | 121.646 | 46.9985 | 30.915 | 69.6356 | 110.0412 | 151.3821 | 326.1856 | 2822.0145
Calice Advanced Manuf | 5.928% | 341.722 | 344.0214 | 270.9412 | 329.2928 | 133.5937 | 87.8711 | 33.9494 | 22.3315 | 50.3013 | 79.4884 | 109.351 | 235.6204 | 2038.4843
Campus Services | 3.807% | 219.475 | 220.9519 | 174.0152 | 211.4922 | 85.8022 | 56.4363 | 21.8044 | 14.3427 | 32.3066 | 51.0523 | 70.232 | 151.33 | 1309.2407
Decker Health | 11.37% | 655.2525 | 659.6616 | 519.5301 | 631.4194 | 256.1662 | 168.493 | 65.0981 | 42.8207 | 96.4528 | 152.419 | 209.6807 | 451.8025 | 3908.7966
Ice Center | 9.461% | 545.399 | 549.0689 | 432.4306 | 525.5616 | 213.2198 | 140.245 | 54.1844 | 35.6418 | 80.2824 | 126.8659 | 174.5276 | 376.0575 | 3253.4845
Library | 7.916% | 456.353 | 459.4237 | 361.8286 | 439.7543 | 178.4079 | 117.3475 | 45.3378 | 29.8226 | 67.1749 | 106.1528 | 146.0329 | 314.6595 | 2722.2955
Natural Science (estim) | 5.793% | 333.9575 | 336.2047 | 264.785 | 321.8107 | 130.5583 | 85.8745 | 33.178 | 21.8241 | 49.1584 | 77.6822 | 106.8664 | 230.2667 | 1992.1665
Old Science | 5.781% | 333.2618 | 335.5043 | 264.2333 | 321.1403 | 130.2863 | 85.6956 | 33.1089 | 21.7786 | 49.056 | 77.5204 | 106.6437 | 229.787 | 1988.0161
Public Safety | 1.66% | 95.6788 | 96.3226 | 75.8609 | 92.1988 | 37.4049 | 24.6031 | 9.5055 | 6.2526 | 14.0839 | 22.256 | 30.6172 | 65.9714 | 570.7557
Student Center | 11.78% | 456.353 | 459.4237 | 361.8286 | 439.7543 | 178.4079 | 117.3475 | 45.3378 | 29.8226 | 67.1749 | 106.1528 | 146.0329 | 314.6595 | 2722.2955
Student Services | 3.241% | 186.8307 | 188.0878 | 148.1325 | 180.0352 | 73.0401 | 48.042 | 18.5613 | 12.2094 | 27.5014 | 43.4589 | 59.7858 | 128.8214 | 1114.5065
Titchener Hall | 7.229% | 416.7604 | 419.5648 | 330.4369 | 401.6019 | 162.9295 | 107.1666 | 41.4044 | 27.2353 | 61.3469 | 96.9431 | 133.3633 | 287.3601 | 2486.1131
Wales Center | 3.651% | 210.4767 | 211.893 | 166.8807 | 202.8212 | 82.2843 | 54.1224 | 20.9105 | 13.7546 | 30.9821 | 48.9592 | 67.3525 | 145.1256 | 1255.5629
Proposed MMBTU Per Building |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Applied Technology | 13.4% | 193.0553 | 242.9429 | 191.3347 | 232.5418 | 94.3419 | 62.0533 | 23.9746 | 15.7702 | 35.522 | 56.1335 | 77.2221 | 166.3917 | 1391.284
BC Center (Child Care) | 0.7825% | 11.278 | 14.1924 | 11.1775 | 13.5848 | 5.5113 | 3.6251 | 1.4006 | 0.92127 | 2.0751 | 3.2792 | 4.5112 | 9.7204 | 81.2769
Business | 8.206% | 118.2673 | 148.8289 | 117.2133 | 142.4571 | 57.7947 | 38.0144 | 14.687 | 9.661 | 21.7611 | 34.3879 | 47.3069 | 101.933 | 852.3127
Calice Advanced Manuf | 5.928% | 85.4305 | 107.5067 | 84.6691 | 102.904 | 41.748 | 27.4597 | 10.6092 | 6.9786 | 15.7192 | 24.8401 | 34.1722 | 73.6314 | 615.6687
Campus Services | 3.807% | 54.8688 | 69.0475 | 54.3798 | 66.0913 | 26.8132 | 17.6363 | 6.8139 | 4.4821 | 10.0958 | 15.9539 | 21.9475 | 47.2906 | 395.4205
Decker Health | 11.37% | 163.8131 | 206.1443 | 162.3532 | 197.3186 | 80.0519 | 52.6541 | 20.3432 | 13.3815 | 30.1415 | 47.6309 | 65.5252 | 141.1883 | 1180.5457
Ice Center | 9.461% | 136.3498 | 171.584 | 135.1346 | 164.238 | 66.6312 | 43.8266 | 16.9326 | 11.1381 | 25.0883 | 39.6456 | 54.5399 | 117.518 | 982.6265
Library | 7.916% | 114.0882 | 143.5699 | 113.0715 | 137.4232 | 55.7525 | 36.6711 | 14.1681 | 9.3196 | 20.9922 | 33.1727 | 45.6353 | 98.3311 | 822.1953
Natural Science (estim) | 5.793% | 83.4894 | 105.064 | 82.7453 | 100.5658 | 40.7995 | 26.8358 | 10.3681 | 6.82 | 15.362 | 24.2757 | 33.3957 | 71.9584 | 601.6797
Old Science | 5.781% | 83.3154 | 104.8451 | 82.5729 | 100.3563 | 40.7145 | 26.7799 | 10.3465 | 6.8058 | 15.33 | 24.2251 | 33.3262 | 71.8084 | 600.4262
Public Safety | 1.66% | 23.9197 | 30.1008 | 23.7065 | 28.8121 | 11.689 | 7.6885 | 2.9705 | 1.9539 | 4.4012 | 6.955 | 9.5679 | 20.6161 | 172.3812
Student Center | 11.78% | 169.8104 | 213.6913 | 168.297 | 204.5425 | 82.9827 | 54.5818 | 21.0879 | 13.8714 | 31.245 | 49.3747 | 67.9241 | 146.3573 | 1223.7663
Student Services | 3.241% | 46.7077 | 58.7775 | 46.2914 | 56.261 | 22.825 | 15.0131 | 5.8004 | 3.8154 | 8.5942 | 13.5809 | 18.6831 | 40.2567 | 336.6064
Titchener Hall | 7.229% | 104.1901 | 131.114 | 103.2615 | 125.5006 | 50.9155 | 33.4896 | 12.9389 | 8.511 | 19.1709 | 30.2947 | 41.676 | 89.8 | 750.8628
Wales Center | 3.651% | 52.6192 | 66.2166 | 52.1502 | 63.3816 | 25.7139 | 16.9133 | 6.5345 | 4.2983 | 9.6819 | 15.2998 | 21.0477 | 45.3518 | 379.2086
graph of yearly delta gas vs electricity |  | Jan: massive reduction of natgas and increase of electricity
Geothermal vs Airsource (Delta 10C) |  | Jan: airsorce wins; Apr: to plot airsource use COP at ambient temp data
Geothermal vs Airsource (Delta 20C) |  | Jan: airsource wins; Apr: Find cop that supports our data
Geothermal vs Airsource (Delta 30C) |  | Jan: geo wins; Feb: we hope; Apr: plot airsoruce vs geothermal
Geothermal vs Airsource (Delta 40C) |  | Jan: geo wins; Feb: we hope; Apr: Geo thermal has smaller delta because ground is warmer
geothermal is capped at delta because ground water never freezes
BTU Required per building by Month |  |  | BTU Geothermal | 1801503712.6844 | 1813625814.8094 | 1428358540.7 | 1735978751.8937 | 704284760.7031 | 463242383.6031 | 178975964.5188 | 117728106.2562 | 265180356.7437 | 419049823.15 | 576480938.1187 | 1242153054.45 | 10746562207.6313
|  |  |  | Current MMBTU | Geothermal MMBTU | ASHP MMBTU
Applied Technology |  | Jan: 83244; Feb: 13.4%; Mar: 4606.5529; Apr: 1391.284
BC Center (Child Care) |  | Jan: 4863; Feb: 0.7825%; Mar: 269.1085; Apr: 81.2769
Business |  | Jan: 50996; Feb: 8.206%; Mar: 2822.0145; Apr: 852.3127
Calice Advanced Manuf |  | Jan: 36837; Feb: 5.928%; Mar: 2038.4843; Apr: 615.6687
Campus Services |  | Jan: 23659; Feb: 3.807%; Mar: 1309.2407; Apr: 395.4205
Decker Health |  | Jan: 70635; Feb: 11.37%; Mar: 3908.7966; Apr: 1180.5457
Ice Center |  | Jan: 58793; Feb: 9.461%; Mar: 3253.4845; Apr: 982.6265
Library |  | Jan: 49194; Feb: 7.916%; Mar: 2722.2955; Apr: 822.1953
Natural Science (estim) |  | Jan: 36000; Feb: 5.793%; Mar: 1992.1665; Apr: 601.6797
Old Science |  | Jan: 35925; Feb: 5.781%; Mar: 1988.0161; Apr: 600.4262
Public Safety |  | Jan: 10314; Feb: 1.66%; Mar: 570.7557; Apr: 172.3812
Student Center |  | Jan: 73221; Feb: 11.78%; Mar: 2722.2955; Apr: 1223.7663
Student Services |  | Jan: 20140; Feb: 3.241%; Mar: 1114.5065; Apr: 336.6064
Titchener Hall |  | Jan: 44926; Feb: 7.229%; Mar: 2486.1131; Apr: 750.8628
Wales Center |  | Jan: 22689; Feb: 3.651%; Mar: 1255.5629; Apr: 379.2086
|  | 621436 |  |  | #REF!
Current Cooling Demand Per Month (2017) |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total |  | hours
Average Ambient Temp |  | 21 | 25 | 34 | 42 | 55 | 65 | 69 | 70 | 60 | 49 | 37.75 | 28
Delta T
MWh |  | 0.08 | 0 | 0.1 | 0.88 | 3.26 | 5.6 | 9.05 | 13.14 | 5.05 | 1.19 | 0.02 | 0 | 38.37 |  | 1000 | 0.03837
Current BTU |  | 272960 | 0 | 341200 | 3002560 | 11123120 | 19107200 | 30878600 | 44833680 | 17230600 | 4060280 | 68240 | 0 | 130918440 | 14945.0274 |  | 3412000000
Geothermal BTU |  | 189252.2667 | 0 | 236565.3333 | 2081774.933 | 7712029.867 | 13247658.67 | 21409162.67 | 31084684.8 | 11946549.33 | 2815127.467 | 47313.0667 | 0 | 90770118.4
Net Savings |  | 83707.7333 | 0 | 104634.6667 | 920785.0667 | 3411090.133 | 5859541.333 | 9469437.333 | 13748995.2 | 5284050.667 | 1245152.533 | 20926.9333 | 0
Cost per KWh (c) |  | 0.173 | 0.175 | 0.17 | 0.173 | 0.185 | 0.193 | 0.194 | 0.186 | 0.188 | 0.187 | 0.178 | 0.17 | 0.181
Cost per MWh |  | 173 | 175 | 170 | 173 | 185 | 193 | 194 | 186 | 188 | 187 | 178 | 170
Month Number
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| COP | January | February | March | April | May | June | July | August | September | October | November | December
Cooling (MBTU) |  | 0 | 0 | 0 | 3.0026 | 11.1231 | 19.1072 | 30.8786 | 44.8337 | 17.2306 | 4.0603 | 0 | 0
90-95 | 4.6334 | 0 | 0 | 0 | 0 | 0.014728 | 0 | 0.014519 | 0.051606 | 0 | 0 | 0 | 0
85-90 | 4.6334 | 0 | 0 | 0 | 0 | 0.014728 | 0.25508 | 0.18875 | 0.18062 | 0 | 0 | 0 | 0
80-85 | 4.6334 | 0 | 0 | 0 | 0 | 0.16201 | 0.4889 | 1.0744 | 1.0579 | 0 | 0 | 0 | 0
75-80 | 4.6334 | 0 | 0 | 0 | 0 | 0.51547 | 0.77586 | 1.539 | 2.3481 | 0.4863 | 0 | 0 | 0
70-75 | 4.6334 | 0 | 0 | 0 | 0 | 0.55965 | 1.0097 | 1.3503 | 2.8641 | 1.1728 | 0 | 0 | 0
65-70 | 4.6334 | 0 | 0 | 0 | 0.64802 | 1.134 | 1.5942 | 2.4973 | 3.1738 | 2.0596 | 0.8763 | 0 | 0
Proposed |  | 0 | 0 | 0 | 0.64802 | 2.4006 | 4.1238 | 6.6643 | 9.6761 | 3.7188 | 0.8763 | 0 | 0
|  | 5764.81 | 5803.6 | 4570.75 | 5555.13 | 2253.71 | 1482.38 | 572.72 | 376.73 | 848.58 | 1340.96 | 1844.74 | 3974.89
OfFset (MWh) |  | -220.289 | -216.9294 | -160.9767 | -222.0347 | -27.0365 | 6.4117 | 65.4641 | 93.7344 | 46.6708 | 20.6558 | 1.6596 | -136.2087
Offset (MMBTU) |  | -751.6261 | -740.1632 | -549.2526 | -757.5823 | -92.2485 | 21.8766 | 223.3636 | 319.8219 | 159.2406 | 70.4775 | 5.6624 | -464.7442
Heating (MMBTU) |  | 5013.1839 | 5063.4368 | 4021.4974 | 4797.5477 | 2161.4615 | 1504.2566 | 796.0836 | 696.5519 | 1007.8206 | 1411.4375 | 1850.4024 | 3510.1458
60-65 | 4 | 0 | 0 | 12.1618 | 80.2937 | 112.344 | 224.2792 | 106.8428 | 109.0132 | 71.7432 | 49.9284 | 3.2125 | 0
55-60 | 4 | 0 | 0 | 51.3498 | 100.3671 | 149.4825 | 71.3616 | 56.5638 | 51.9111 | 68.3268 | 54.2491 | 30.84 | 2.359
50-55 | 3.98 | 0 | 0 | 57.0402 | 164.7567 | 121.3067 | 30.7372 | 23.8622 | 12.3315 | 37.3394 | 46.3194 | 25.1835 | 5.9271
45-50 | 3.98 | 72.7991 | 1.8932 | 63.8307 | 322.7887 | 73.7171 | 28.4604 | 11.9311 | 0.94858 | 51.5026 | 81.5414 | 43.9096 | 24.8936
40-45 | 3.95 | 63.1169 | 49.5967 | 57.4734 | 257.4819 | 65.8151 | 19.5 | 0 | 0 | 13.4059 | 69.5206 | 73.5216 | 32.2492
35-40 | 3.74 | 93.6855 | 70.5135 | 171.9849 | 202.1655 | 18.8672 | 2.4229 | 0 | 0 | 10.9615 | 36.4553 | 163.5457 | 148.8547
30-35 | 3.72 | 206.4917 | 261.2901 | 281.8861 | 53.9608 | 1.9967 | 0 | 0 | 0 | 0 | 16.5189 | 121.5916 | 210.5316
25-30 | 3.74 | 136.925 | 261.9075 | 135.8536 | 19.6798 | 0 | 0 | 0 | 0 | 0 | 3.5942 | 22.6765 | 136.2399
20-25 | 3.74 | 248.6269 | 225.6434 | 93.9413 | 23.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.254
15-20 | 3.74 | 142.3299 | 269.9662 | 101.1676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160.2081
2021-10-15 | 3.74 | 142.3299 | 114.8363 | 26.0145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.1059
2021-05-10 | 3.36 | 116.3133 | 91.9434 | 9.6522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.2332
0-5 | 3.36 | 86.2323 | 15.6977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-5-0 | 3.36 | 38.1026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-10--5 | 3.36 | 12.0324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total MMBTU (Proposed) |  | 1358.9856 | 1363.2879 | 1062.356 | 1224.7521 | 543.5293 | 376.7614 | 199.1999 | 174.2044 | 253.2794 | 358.1272 | 484.4809 | 936.8563
Proposed Therm consumption |  | 135898.5565 | 136328.7854 | 106235.603 | 122475.2138 | 54352.9307 | 37676.1375 | 19919.986 | 17420.4378 | 25327.9441 | 35812.7216 | 48448.094 | 93685.6273
THerm (Current) |  | 57661.9 | 58049.9 | 45718.4 | 55564.6 | 22542.5 | 14827.3 | 5728.6 | 3768.2 | 8487.8 | 13412.8 | 18451.8 | 39758.4

## Sources To do
Sources
Electricity growth rate | https://www.nyiso.com/documents/20142/2223020/2018-Power-Trends.pdf/4cd3a2a6-838a-bb54-f631-8982a7bdfa7a
Air source COP at ambient temps | https://www.researchgate.net/figure/COP-of-the-heat-pump-at-different-ambient-air-temperatures-for-condenser-outlet_fig7_272093420
geothermal COP values | https://www.pickhvac.com/faq/heat-pump-cop/
NYS Cost of elec | https://www.nyserda.ny.gov/Researchers-and-Policymakers/Energy-Prices/Electricity/Monthly-Avg-Electricity-Residential
Mistubishi air source | https://www.mitsubishipro.com/pdfs/m-series-catalog.pdf
Entering Water Temperture Chart | https://www.researchgate.net/publication/314106888_Nanocomposite_Materials_Used_for_Ground_Heat_Exchanger_Pipes